| Monthly Safety/Emergency Management Committee Meeting FINAL January meeting for December 2025 DOCUMENTATION |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Call to order: Date: January 21, 2026 |  |  |  |  |  |  |  |  |  |  |  |  |
| Safety/Emergency Management Meeting Reporting for December 2025, |  |  |  |  |  |  |  |  |  |  |  |  |
| Members: |  |  | Janice Merrill, Facilities, Brenda Jennings, IC., Brendan Price, CNO, Chasity Richardson, Adm/HR, Devina Perez, Admissions, Holly Masquieler-Woodson, Materials, Jackoa Lemmons, Radiology |  |  |  |  |  |  |  |  |  |
| 1. |  | Safety Committee Meeting opened at: 1303 Date: January 21, 2026 Motion to open meeting by Len Lacefield, Second by Devina Perez, all in favor. yea |  |  |  |  |  |  |  |  |  |  |
| 2. |  | Motion to accept meeting minutes from the last meeting conducted December 17, 2025, by: Brenda Jennings and second by: Len Lacefield all in favor. Yea |  |  |  |  |  |  |  |  |  |  |
| Topic |  |  |  | Discussion |  |  |  | Action |  |  | Person Responsible |  |
| OLD BUSINESS: |  |  |  |  |  |  |  |  |  |  |  |  |
| A. | Air Born Isolation Monitors |  |  | A. |  | Monitors for both Med Surg and ER are being monitored with a Manometer until monitors have been installed |  | A. | Motion to accept air born isolation monitoring. Safety Committee members accepted the reports as presented |  | A. | Janice Merrill |
| B. | Active Shooter Drill |  |  | B. |  | An active shooter drill will be conducted in the ER. |  | B. | Follow up drill was held on 12.16.25. After action report presented to ER manager and Life Safety for approval. |  | B. | Asher Reed |
| C. | Exhaust Fan 140’s hall |  |  | C. |  | The exhaust fan for the 140’s hall has not been completed. |  | C. | No action needed for acceptance at this time. Report for completion will be brought back when completed |  | C. | Janice Merrill |
|  | Motion made to accept old business by Devina Perez and 2nd by Brenda Jennings all members accepted |  |  |  |  |  |  |  |  |  |  |  |
| New Business |  |  |  |  |  |  |  |  |  |  |  |  |
| A. | Quarterly Fire Drill Report |  |  | A. |  | The quarterly fire drill |  | A. | Documentation will be attached |  | A. | Janice Merrill |
| B. | IT Drill for Security |  |  | B. |  | IT team has recommended that CRH Adm/employees to participate in the Security Awareness Training Program. |  | B. | No action needed for acceptance of IT Drill. The IT Drill Report will be brought back to the next meeting. |  | B. | Brenda Jennings |
| C. | Quarterly Fire Alarm/Sprinkler Inspection Report |  |  | C |  | Quarterly fire sprinkler testing. |  | C | No action needed for ¼ testing |  | C | Janice Merrill |
| D. | Incident Report: Staff, Patient and/or Visitor |  |  | D |  | Nothing to report |  | D |  |  | D | Facilities |
| E. | Security Cameras |  |  | E |  | State inspection for Pharmacy requested a camera to be installed in “drug room vault” |  | E | Camera has been installed into the “drug room vault”. Also, a camera was added to the NW door ER side. Completed 12.30.25 |  | E | Facilities |
|  | Motion made to accept old business by Brenda Jennings and 2nd by Jackoa Lemons all members accepted |  |  |  |  |  |  |  |  |  |  |  |
|  | Plan of Correction ACHC Survey |  |  |  |  |  |  |  |  |  |  |  |
| A. | 11.07.03 Monitoring Pressurized Rooms |  |  | A. |  | Ventilation monitoring for clean rooms on Med Surge floor and other locations. Clean room tested positive with the Van o Meter on Med Surg. Clean and dirty rooms through the facility are to be monitored monthly with the Van O Meter as per the ACHC Plan of Correction. No issues currently in the report Documentation will be forwarded to the Life Safety Committee |  | A. | A motion to accept air flow pressure monitoring for the clean room log. Second, all safety committee members, are in favor of the motion. |  | A. | Janice Merrill |
| B. | 13.01.04 Power assist doors |  |  | B. |  | Powered assist doors have been repaired and are all on the lock down system controlled by the fire alarm system. ER department doors are monitored monthly to ensure they are working appropriately. Documentation will be forwarded to the Life Safety Committee. |  | B. | A motion to accept power assist doors. Second, all safety committee members, are in favor of the motion. |  | B. | Janice Merrill |
| C. | 13.01.06 Egress door |  |  | C. |  | The Egress door located on the west side of the building releases with activation of motion sensor and the emergency release button located adjacent to the door. Egress Doors are monitored monthly & documentation will be forwarded to the Life Safety Committee for reporting. |  | C. | A motion to accept egress doors. Second, all safety committee members, are in favor of the motion. |  | C. | Janice Merrill |
| D. | 13.02.01 Annual testing on the dampers. |  |  | D. |  | Damper inspection with no issues noted |  | D. | No issues noted at this time. |  | D. | Janice Merrill |
| E. | 13.03.09 Fire Extinguisher found on floor. |  |  | E. |  | A fire extinguisher found on the floor in a corner of the MRI room during the January survey is being monitored to be hung and ready for use. Fire Extinguisher is hung and ready for use. Documentation log will be forwarded to the Life Safety Committee monthly |  | E. | A motion to accept fire extinguisher report. Second, all safety committee members, are in favor of the motion. |  | E. | Janice Merrill |
| F. | 13.05.04 Generator Battery Conductance test |  |  | F. |  | Generator battery conductance testing is monitored and signed. Documentation will be forwarded to the Life Safety Committee for acceptance |  | F. | A motion to accept battery conductance test. Second, all safety committee members, are in favor of the motion. |  | F. | Janice Merrill |
| G. | 13.05.09 Utility panels are to be locked and lock out tag out should be used on the breakers if not in use. |  |  | G. |  | Electrical utility panels are checked monthly and documented as locked and secure in the kitchen and all areas. Documentation will be forwarded to the Life Safety Committee monthly for acceptance. |  | G. | A motion to accept utility panels. Second, all safety committee members, are in favor of the motion. |  | G. | Janice Merrill |
|  | Motion made to accept POC ACHC by Brenden Price and 2nd by Chasity Richardson all members accepted |  |  |  |  |  |  |  |  |  |  |  |
|  | Monthly Safety Officer Report |  |  |  |  | Safety Officer report identified on going monitoring as complying. The Life Safety Officer Report will be forwarded to the Life Safety Committee monthly for acceptance. |  |  | A motion to accept monthly safety officer report. Second, all safety committee members, are in favor of the motion. |  |  | Janice Merrill |
| A. | Eye Wash Weekly Run Monthly Report |  |  | A. |  | Supporting documentation is provided to ensure systems are monitored Eye Wash Weekly Run |  | A. | Documentation is attached |  | A. | Facilities |
| B. | Monthly Fire Suppression Gauge reading, Control Valve, and twin Connection Inspection |  |  | B. |  | Supporting documentation is provided to ensure systems monitored for monthly fire suppression, gauge reading, control valve and twin connection. |  | B. | The fire dept hook up on the north end of building located by the parking lot has a leak. Follow up with City of Clinton. |  | B. | Facilities |
| C. | Monthly Portable Fire Extinguishers Report |  |  | C. |  | Supporting documentation is provided to ensure systems are monitored when doing the monthly fire extinguishers / checklist. |  | C. | Fire extinguishers checked no issues noted at this time. Documentation is attached |  | C. | Facilities |
| D. | Daily Air Flow & Humidity reports for OR 1, OR 2 and Procedure Room |  |  | D. |  | Supporting documentation is provided to ensure systems are monitored when doing OR 1, OR 2, and procedure room |  | D. | Documentation is attached |  | D. | Facilities |
| E. | ACH Annual Inspection Report |  |  | E. |  | The ETO Sterilizer room: The exhaust in this room is below the amount needed to achieve negative pressure or the air changes required. Room would require a minimum of 100 CFM exhaust airflow to achieve negative pressure and 10 ACH. |  | E. | Due to the department being closed we will schedule for them to come and check at a later date. |  | E. | Janice Merrill |
| F | Monthly Egress Lights Testing Report |  |  | F |  | Supporting documentation is provided to ensure systems are monitored when doing the monthly egress lights |  | F | Documentation is attached |  | F | Facilities |
| G | Annual Boiler License Report |  |  | G |  | Next boiler inspection is scheduled for Boiler 1 in January 2026 |  | G |  |  | G | Facilities |
| H | Monthly Exit Signs |  |  | H |  | Supporting documentation is provided to ensure systems are monitored when doing the monthly exit lights |  | H | Documentation is attached |  | H | Facilities |
| I | Weekly Emergency Generator Inspection |  |  | I |  | Supporting documentation is provided to ensure systems are monitored when doing the weekly generator test |  | I | Documentation is attached |  | I | Facilities |
| J | Monthly Generator and Transfer Switch Inspection |  |  | J |  | Supporting documentation is provided to ensure systems are monitored when doing the monthly generator and transfer switch test |  | J | Documentation is attached |  | J | Facilities |
| K | Monthly Battery Backup Lights for OR and Transfer Switch |  |  | K |  | Supporting documentation is provided to ensure systems are monitored when doing the monthly battery backup lights |  | K | Documentation is attached |  | K | Facilities |
| L | Monthly Medical Gas Inspection |  |  | L |  | Supporting documentation is provided to ensure systems are monitored when doing the monthly medical gas inspection. In the process of purchasing Nitrogen (liquid) for the Dermatologist. Will check the requirements |  | L | Documentation is attached |  | L | Facilities |
| M | Monthly Recall and Product Notifications |  |  | M |  | 12.16.25: We received a product notification regarding several BD Alaris pump module sets being discontinued to streamline BD’s product portfolio. After examining the list, it was found that none of the items were kept in the storeroom. The response form was completed accordingly and returned to the manufacturer via email. No further action is required. 12.29.25: We received product notification in reference to a compatibility issue with MAS Bilirubin controls, as they generated higher-than-expected results during the value-assignment process for Gens 19 and aboce of Vitros TBIL slides and Vitros XT TBIL-ALKP slides. A copy of this notice was provided to the lab director. No response form was supplied, and no product returns were needed. No further action is required. |  | M | A motion to accept monthly recalls and notifications report. Second, all safety committee members, are in favor of the motion. |  | M | Holly Masquelier Materials |
| N | Biohazard Manifests Monthly Report |  |  | N |  | No pickup November 2025 |  | N | Documentation is attached |  | N | Facilities/EVS |
| O | Bio Medical Monthly Report |  |  | O |  | Supporting documentation is provided to ensure system/processes are being monitored. Work order for Bio Med was created and uploaded to the shared drive Biomed here December 15, 2025 inspected 4 pieces of equipment inspected throughout the building. |  | O | Documentation is attached. |  | O | Facilities |
| P | Seldom Used Fixtures Monthly Report |  |  | P |  | Supporting documentation is provided to ensure system/processes are being monitored. |  | P | Documentation is attached |  | P | Facilities |
| Q | Boiler Water Treatment Monthly Report |  |  | Q |  | Boiler # 1: Conductivity and Alkalinity below range. Boiler # 2: Conductivity and Alkalinity below range. Water Softener: No salt Cooling Tower: Conductivity and inhibitor level within range. Chill Water Loop: Nitrite level within range. Hot Water Loop: Nitrite level within range Recommendations: Get salt for water softener. Continue current testing. Consequences: Hard water is killing your boilers. They will scale up and you will have to have them acid cleaned. Very Expensive. Continue current program. |  | Q | Documentation is attached. |  | Q | Facilities |
| R | Pest Control (Monthly) |  |  | R |  | Services conducted on 12.29.25 Inspected and treated interior perimeter for general pests. Serviced common areas, storage areas, conference and offices, kitchen and break rooms and restrooms. Serviced all glue monitors for general pests. Serviced all exterior bait stations and replaced bait as needed. |  | R | Documentation is attached |  | R | Facilities |
| S | EOC Rounds |  |  | S |  | All depts from July – December 2025 |  | S | Document is attached |  | S | Facilities |
| T | State Inspections: |  |  | T |  |  |  | T |  |  | T |  |
|  | Motion made to accept Monthly Life Safety Meeting by Chasity Richardson and 2nd by Devina Perez all members accepted |  |  |  |  |  |  |  |  |  |  |  |
|  | Adjourn |  |  |  |  | Motion to adjourn and to meet in February 2026 |  |  | At 1317 made a motion to adjourned by and 2nd all, in favor. Yea |  |  | Life Safety Minutes and Documentation will be forwarded to Medical Staff Committee for review and approval |