| CLINTON REGIONAL HOSPITAL |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Monthly Safety/Emergency Management Committee Meeting |  |  |  |  |  |  |  |  |  |
| Call to order: Date: August 7, 2024 |  |  |  |  |  |  |  |  |  |
| Safety/Emergency Management Meeting Reporting for JULY 2024 |  |  |  |  |  |  |  |  |  |
| Members: |  |  | Len Lacefield, CEO, Brenda Jennings, RN IC/Quality, Holly Masquelier, Purchasing Agent, Sarah Keys, EVS, Janice Merrill, Facilities, David Barnett, Radiology, Devina Perez, Admissions, Chasity Richardson, Adm. Asst/HR, Stephanie Bustos, AP, Stephanie Drum, Cardiopulmonary, Brendan Price, RN CNO, Cris Hickerson, Pharmacy. |  |  |  |  |  |  |
| 1. |  | Safety Committee Meeting opened at: 1300 Date: September 4, 2024, Motion to open meeting by: Cris Hickerson, Second by: Brenda Jennings, all in favor. yea |  |  |  |  |  |  |  |
| 2. |  | Motion to accept meeting minutes from last meeting conducted August 7, 2024, by: Cris Hickerson, Pharmacy and Second by: David Barnett, all in favor. Yea |  |  |  |  |  |  |  |
| Topic |  |  |  | Discussion |  | Action |  | Person Responsible |  |
| OLD BUSINESS: |  |  |  |  |  |  |  |  |  |
| A. | Air Born Isolation Monitors |  |  | A. | Monitors for both Med Surg and ER are being monitored with a Manometer until monitors have been installed | A. | S. Bustos made a motion to accept air born isolation monitoring. Second by L. Lacefield, all Safety Committee members accepted the reports as presented | A. | Janice Merrill |
| B. | Active Shooter Drill |  |  | B. | An active shooter drill will be conducted in the ER. Will speak with new ER Director about planning drill. | B. | No action needed | B. | Anita Ford, ER Director Janice Merrill, Facilities |
| C | Access Control System/Magnetic Locks |  |  | C | The doors to the ER have been repaired and are working appropriately with the access system. | C | No action needed | C | Janice Merrill |
| D. | Motor for HVAC equipment |  |  | D. | Received a quote from Matherly Mechanical for $6500.00 to replace the motor in the AHU by Pharmacy. The process of looking for a motor that is the most cost effective. Currently the motor functions are winning but has not gotten any worse and is functioning. | D. | No action needed for acceptance at this time. Report for completion will be brought back in the next meeting. | D. | Janice Merrill |
| E. | Exhaust Fan 140’s hall |  |  | E. | The exhaust fan for the 140’s hall has not been completed. In the process of looking for a motor that is the most cost effective. | E. | No action needed for acceptance at this time. Report for completion will be brought back in the next meeting. | E. | Janice Merrill 1 |
| New Business |  |  |  |  |  |  |  |  |  |
| A. | Roof Leaks |  |  | A. | After the last rain the North end of the building started leaking. In the process of getting quotes on for repairs. Working on when the roof was replaced last. | A. |  | A. | Janice Merrill |
| B. | Underground Storage Tank (Generator) |  |  | B. | OCC here on 7/8/24 for the underground storage tank. #1 NOV was 5 days non-compliant of measuring the tank and a new stick that has 1/8” inches marked on it. #2 when non-compliant on tank/paperwork the operator training is to be renewed within 30 days. | B. | OCC is scheduled for re-inspection on 8/9/24. New stick obtained Craig Wagner and Janice Merrill are certified as of 7/17/24 until 7/1/27. | B. | Janice Merrill |
| C. | Quarterly Fire Drill Report |  |  | C | The quarterly fire drill is scheduled on the 7a shift. | C | No action needed for acceptance at this time. Report for completion will be brought back in the next meeting. | C | Janice Merrill |
| D | IT Drill for Security |  |  | D | IT team has recommended that CRH Adm/employees to participate in the Security Awareness Training Program. Contact Brenda Jennings for Jerry Hartman on results of the drill. Documentation will be presented at the next meeting. Received info on types of drills that can be performed. - Phishing Simulations (done) - Tabletop exercises (Trubridge) - Vulnerability (3rd party vendor) Scanning/Penetration Testing - Data Backup and Disaster Recovery testing. (cannot due Trubridge holds data) https://www.vc3.com/blog/cyber-security-drills (info on drills) User awareness training was done on 6.28.24 Documentation will be forwarded to the Life Safety Committee | D | No action needed for acceptance of IT Drill. The IT Drill Report will be brought back at the next meeting. | D | Brenda Jennings Jerry Hartman 2 |
|  | Plan of Correction ACHC Survey |  |  |  |  |  |  |  |  |
| A. | 11.07.03 Monitoring Pressurized Rooms |  |  | A. | Ventilation monitoring for clean rooms on Med Surge floor and other locations. Clean room tested positive with the Van o Mete on Med Surg. Clean and dirty rooms through the facility are to be monitored monthly with the Van O Meter as per the ACHC Plan of Correction. No issues currently in the report Documentation will be forwarded to the Life Safety Committee | A. | Cris Hickerson made a motion to accept air flow pressure monitoring for the clean room log. Seconded by Chasity Richardson all safety committee members in favor of the motion. | A. | Janice Merrill |
| B. | 13.01.04 Power assist doors |  |  | B. | Powered assist doors have been repaired and are all on the lock down system controlled by the fire alarm system. ER department doors are being monitored monthly to ensure they are working appropriately. Documentation will be forwarded to the Life Safety Committee. | B. | Cris Hickerson made a motion to accept the ER Door Monitoring report. Seconded by Stephanie Drum, all safety committee members in favor of motion. | B. | Janice Merrill |
| C. | 13.01.06 Egress door |  |  | C. | The Egress door located on the west side of the building releases with activation of motion sensor and the emergency release button located adjacent to the door. Egress Doors are monitored monthly & documentation will be forwarded to the Life Safety Committee for reporting | C. | Devina Perez made a motion to accept egress magnetic door release report. Seconded by Cris Hickerson, all safety committee members are in favor of the motion. | C. | Janice Merrill |
| D. | 13.02.01 Annual testing on the dampers. |  |  | D. | 7/18/24 damper issue has been resolved and has been added to the programmer report. ACHA notified. This has been completed | D. | Stephanie Drum made a motion to accept the damper report. Seconded by Chasity Richardson, all safety committee members are in favor of the motion. | D. | Janice Merrill |
| E. | 13.03.09 Fire Extinguisher found on floor. |  |  | E. | A fire extinguisher found on the floor in a corner of MRI room during January survey is being monitored to be hung and ready for use. Fire Extinguisher is hung and ready for use. Documentation log will be forwarded to the Life Safety Committee monthly | E. | Chasity Richardson_ made a motion to accept the MRI Fire Extinguisher monitoring report. Seconded by Brenda Jennings all safety committee members in favor of the motion. | E. | Janice Merrill 3 |
| F. | 13.05.04 Generator Battery Conductance test |  |  | F. | Generator battery conductance testing is monitored and signed and dated for the month of July 2024 Documentation will be forwarded to the Life Safety Committee for acceptance | F. | Chasity Richardson a made motion to accept battery conductance monitoring report for July. Seconded by Cris Hickerson, all safety committee members in favor of motion | F. | Janice Merrill |
| G. | 13.05.09 Utility panels are to be locked and lock out tag out should be used on the breakers if not in use. |  |  | G. | Electrical utility panels are checked monthly and documented as locked and secure in the kitchen and all areas. Documentation will be forwarded to the Life Safety Committee monthly for acceptance. | G. | Chasity Richardson a made motion to accept the Electrical Panel monitoring report for July. Seconded by Cris Hickerson, all safety committee members are in favor of motion. | G. | Janice Merrill |
|  | Monthly Safety Officer Report |  |  |  | Safety Officer report identified on going monitoring as complying. Life Safety Officer Report will be forwarded to the Life Safety Committee monthly for acceptance. |  | Chasity Richardson made motion to approve safety officer report, second by Cris Hickerson and all members in favor of the motion |  | Janice Merrill |
| A. | Eye Wash Weekly Run Monthly Report |  |  | A. | Supporting documentation is provided to ensure systems are monitored Eye Wash Weekly Run | A. | Documentation is attached | A. | Facilities |
| B. | Monthly Fire Suppression Gauge reading, Control Valve, and twin Connection Inspection |  |  | B. | Supporting documentation is provided to ensure systems monitored for monthly fire suppression, gauge reading, control valve and twin connection | B. | Documentation is attached. | B. | Facilities |
| C. | Monthly Portable Fire Extinguishers Report |  |  | C. | Supporting documentation is provided to ensure systems are monitored when doing the monthly fire extinguishers / checklist. | C. | Documentation is attached | C. | Facilities |
| D. | Daily Air Flow & Humidity reports for OR 1, OR 2 and Procedure Room |  |  | D. | Supporting documentation is provided to ensure systems are monitored when doing OR 1, OR 2, and procedure room | D. | Documentation is attached | D. | Facilities |
| E. | Monthly Egress Lights Testing Report |  |  | E. | Supporting documentation is provided to ensure systems are monitored when doing the monthly egress lights | E. | Documentation is attached | E. | Facilities |
| F. | Annual Boiler License Report |  |  | F. | Boiler # 2 due for inspection in July 2024 (7.23.24) No issues at the time of inspection. Boiler #1 annual inspection was held on 1/30/24. | F. | Nothing to report currently. | F. | Facilities 4 |
| G. | Monthly Exit Signs |  |  | G. | Supporting documentation is provided to ensure systems are monitored when doing the monthly exit lights | G. | Documentation is attached | G. | Facilities |
| H. | Weekly Emergency Generator Inspection |  |  | H. | Supporting documentation is provided to ensure systems are monitored when doing the weekly generator test | H | Documentation is attached | H. | Facilities |
| I. | Monthly Generator and Transfer Switch Inspection |  |  | I. | Supporting documentation is provided to ensure systems are monitored when doing the monthly generator and transfer switch test | I. | Documentation is attached | I. | Facilities |
| J. | Monthly Battery Backup Lights for OR and Transfer Switch |  |  | J. | Supporting documentation is provided to ensure systems are monitored when doing the monthly battery backup lights | J. | Documentation is attached | J. | Facilities |
| K. | Monthly Medical Gas Inspection |  |  | K. | Supporting documentation is provided to ensure systems are monitored when doing the monthly medical gas inspection. | K. | Documentation is attached | K. | Facilities |
| L. | Monthly Recall for Purchasing Supplies |  |  | L. |  | L. |  | L. | Facilities/Materials |
|  | ---Product Notifications/Recalls - Equipment Notifications/Recalls |  |  |  | - On 7/9, we received a product correction notification from Getinge regarding specific models of Atrium chest drains that lack sufficient precaution instructions for proper setup of catheters and patient tube connections. I located the chest drains we have on hand, which are in the ER. We did have one of the affected models, 2002-300. I taped a copy of the product correction warning poster to the one chest drain we had that was affected, so anyone who intends to use the item will see the necessary information. I also emailed nursing leadership to inform them of the notification. I completed the product response form accordingly the same day and emailed it back to the manufacturer. No further action is required at this time. - On 7/16, we received a drug notification regarding potassium chloride ER capsules. I took this notification to the pharmacy and verified with Cathy Bridges that we did not have the affected product listed in the notification. I completed the product response form accordingly and returned it to the manufacturer via email the same day. There is no further action required. - On 7/17, we received an equipment notification from GE Healthcare, regarding our Proteus XR/a machine, located in Radiology. I took the notification to David (Radiology Director) and confirmed that we do have the equipment. The notice stated the machine does not have a de-installation manual describing process steps for de-installing the device. These steps must be followed when de-installing the device. Since we are not planning to do any de-installation for the equipment at this time, I emailed the notice to our Radiology Director in case this information is needed in the future. I completed the product response form the same day and returned it to the manufacturer via email. There is no further action required at this time |  | Stephanie Drum made a motion to accept recalls for purchasing supplies. Second by Cris Hickerson, all Safety Committee members accepted the reports as presented |  | Holly Masquelier 5 |
| M. | Biohazard Manifests Monthly Report |  |  | M. | Supporting documentation is provided to ensure system/processes are being monitored. Biohazard pickups are scheduled for every other month. July pickup 17-31 gal tubs (allotted 8) Also 4–17-gal tubs (1=Pharmacy) total of 767#. 21 total tubs picked up -8 allotted over by 13 tubs. There is not enough patient care in, lab, er, ms to justify this amount. Spot check Biohazard to see if appropriate items are being placed. Tabled until next meeting | M. |  | M. | Facilities/EVS 6 |
| N. | Bio Medical Monthly Report |  |  | N. | Supporting documentation is provided to ensure system/processes are being monitored. Biomed here July 8-10, 2024 35 pieces of equipment inspected throughout the building. Spoke with biomed tech in regards to a wireless alarm for Lab to sound in ER. Has not found a wireless one that will work. Currently the alarm is located at the main surses station and works appropriately the issues is the desk is not monitored like it has been in the past. | N. | Documentation is attached. | N. | Facilities |
| O. | Seldom Used Fixtures Monthly Report |  |  | O. | Supporting documentation is provided to ensure system/processes are being monitored. | O. | Documentation is attached | O. | Facilities |
| P. | Boiler Water Treatment Monthly Report |  |  | P. | Supporting documentation is provided to ensure system/processes are being monitored. 7/9/2024: Boiler #1: Conductivity and Chemical levels within range. Boiler #2: Conductivity and Chemical level within range. The water softener working properly at the time of testing. Cooling Tower: Conductivity within range. Inhibitor level below range. Chill Water Loop: Nitrite level at the bottom of the range Hot Water Loop: Nitrite level at the bottom of the range. Cooling Tower: Increased Speed and Stroke on inhibitor feed pump 10%. Recommendations: Cooling tower: increased speed and stroke 10% inhibitor feed pump. GC will order inhibitor for loops and add on next service. Continue current testing. | P. | Documentation is attached. | P. | Facilities |
|  |  |  |  |  |  |  |  |  | 7 |
| Motion to accept Monthly Consent Reports: Chasity Richardson and 2nd Stephanie Drum. All in favor: yea |  |  |  |  |  |  |  |  |  |
|  | Adjourn |  |  |  | Motion to adjourn and to meet on September 4, 2024 |  | Cris Hickerson made motion to adjourned @ 1328 and 2nd by Devina Perez all in favor. Yea |  | Life Safety Minutes and Documentation will be forwarded to Medical Staff Committee for review and approval 8 |